## Cover Sheet
Center of Standardization Standard Design Compliance Checklist
Center of Standardization for Army Aviation Facilities (Vertical)
U.S. Army Corps of Engineers, Mobile District (CESAM)
Latest Revision: 2026-03
Instructions:
1. Design Agent should rename file to add P2 Project Number at beginning of file name.
2. Design Agent should edit submission column headers to reflect local submission practice (35,65,95,100, etc.)
3. For each submission, designers shall review and address compliance items where applicable.
4. Place designer initials or N/A in submission column.
5. Include checklist with submission documents.
6. COS will review design and checklist and provide comments where necessary.
COS Contacts:
Program Manager: | Daniel.E.Bush@usace.army.mil | (251) 694-3788
Technical Lead:
Legend:
Lessons Learned Item - for designer reference and discussion with users, DPW, etc.
Required COS Compliance item - to be addressed and reviewed at each submission

## Programming_Planning
Programming
# | Compliance Item | Impacts / Details | 35% | 65% | 100% | COS Notes
PR-01 | Verify if using unit has an overwater mission? | ALSE shop storage room size may be larger to accommodate servicing and storage or life rafts, breathing devices, oxygen bottles, etc.
PR-02 | Verify if using unit has high-altitude mission requirements? | May require oxygen generator system if none available in existing CAB facilities. O2 generator is typically located at ASB; no allowance for individual hangars to have generators if there is a supporting ASB.
PR-03 | Verify that FAA site approval has been initiated and is on track for approval prior to solicitation.
PR-04 | Verify that selected site is consistent with Area or Airfield Development Plan (ADP).
PR-05 | Ensure standard modules sizes as defined in the Army Standard for Aviation Maintenance Hangar Complex and aircraft clearances as defined in UFC 4-211-01 are followed. Additional structural areas might be required for supporting larger door openings.
PR-06 | For facilities remote to main post accommodations (dining, physical fitness, primary motor pool, fuel points, etc.), consider adding space for interior exercise, exterior dedicated fuel truck parking with spill containment, etc.
PR-07 | For facilities used by both permenant party and rotational units (NTC, JRTC, etc.), consider increases to required admin space, secure storage space, toilet/shower facilities and supporting infrastructure.
PR-08 | For facilities with high contractor / manufacturer support civilian personnel, consider increases to admin, secure storage and shop spaces.
Legend:
Lessons Learned Item - for designer reference and discussion with users, DPW, etc.
Required COS Compliance item - to be addressed and reviewed at each submission

## Civil
Civil Site / Utilities
# | Compliance Item | Impacts / Details | 35% | 65% | 100% | COS Notes
CS-01 | Ensure facility siting complies with unobstructed airspace and safety per UFC 3-260-01.
CS-02 | Ensure airfield security is maintained. | Prevent unauthorized access to facility and airfield.
CS-03 | Include drawings and details for GSE and ASIOE covered storage areas | Covered storage typically enclosed with chain link fencing; provide multiple large swing gates.
CS-04 | Ensure UFGS SECTION 01 78 23 requires Occupant Operations Manual and Video Recordings of all Building System Training for all underground utilities including foam containment vessel and oil/water separator.
CS-05 | Include drawings and details for wash rack.
CS-06 | Ensure exterior space with power connections is provided for mobile shop sets.
CS-07 | Airfield pavements must be submitted to Transportation Center of Experise, Omaha District, for review at 35%. | Contact: Transportation Systems Center of Expertise Address: 1616 Capitol Ave., Omaha, NE 68102 Website: https://transportation.erdc.dren.mil/tsmcx/contact.aspx Phone: (402) 995-2399
CS-08 | All hangars are to provide permanent Wash Rack/Wash Apron utilities served from a dedicated utility space and supplied to Apron service points: - Cold Water - Hot Water - Electrical - Compressed Air - Detergent/Water solution containment and mixing - Apron Lighting (comply with Airfield lighting standards) Refer to UFC 3-260-01 for additional details. | Aircraft washing is a required maintenance activity.
Legend:
Lessons Learned Item - for designer reference and discussion with users, DPW, etc.
Required COS Compliance item - to be addressed and reviewed at each submission

## Structural
Structural
# | Compliance Item | Impacts / Details | 35% | 65% | 100% | COS Notes
ST-01 | Max slope of maintenance bay slab is 1/4"/foot to facilitate weighing of aircraft | Army weighing policies and equipment cannot accommodate cross slope greater than 1/4"/foot.
ST-02 | Include drawings and details for GSE and ASIOE covered storage areas
ST-03 | Hangar bay slab meets UFC 4-211-01 criteria (loading, jointing, etc.)
ST-04 | Are bridge cranes clearly shown and coordinated (supports, rails, coverage)
ST-05 | Ensure the correct Risk Category is used for MEDEVAC area. | Reference UFC-4-211-01 3-4.
ST-06 | Coordinate the Hangar Bay floor slope with adjacent floor levels.
ST-07 | Verify footing elevation at emergency shower locations.
ST-08 | Provide roof top Antenna Platform with antennae anchoring. Provide access preferably from interior space or by exterior ladder.
Legend:
Lessons Learned Item - for designer reference and discussion with users, DPW, etc.
Required COS Compliance item - to be addressed and reviewed at each submission

## Architectural
Architectural
# | Compliance Item | Impacts / Details | 35% | 65% | 100% | COS Notes
AR-01 | Ensure compliance with UFC-4-211-01 Aircraft Maintenance Hangars. | Check for adjacencies, clearances and obstructions, life safety, fire protection, and finishes.
AR-02 | Ensure compliance with Standard Design and Room Data Sheet within as applicable. | Check for specific requirements.
AR-03 | Epoxy floor coating manufacturers all require a specific (very low) moisture content in cured concrete slab before their membrane can be applied. UFGS sections require application of a curing compound to hold moisture in. Feedback from USACE construction offices indicate that contractors have used a floor barrier membrane to 'seal' the floor prior to epoxy application citing that the epoxy manufacturer's required moisture content of the slab is unachievable due to the curing compound application required by spec. Options are to require a non‐compound type cure (blankets, water, etc.) for the hangar slab or require the wax type curing compound to be removed after x days, or easiest require a concrete sealer that is compatible with the manufacturers epoxy membrane. | Careful coordination is required to avoid change orders
AR-04 | Bird netting system in maintenance bay must be coordinated in height with the cranes, lights, sag, etc.
AR-05 | If low slope roofs are provided, provide parapets that meet fall protection and fire protection requirements. Recommend minimum parapet height of 48 inches. | Parapets sized for fall protection eliminates temporary or permanent tie off points and facilitates regular maintenance activities without extensive setup of safety equipment.
AR-06 | Include drawings and details for GSE and ASIOE covered storage areas
AR-07 | Ensure elevator hoistway is sized to include entrapment area per Elevator UFC | Standard Design plans are adequate in size for both entrapment and stretcher sized cab.
AR-08 | Provide controls for overhead coiling doors from shops to hangar bay on both sides of door.
AR-09 | Are bridge cranes shown on all plans , RCPs, sections and coordinated with other disciplines?
AR-10 | If translucent windows or clearstory panels are used for daylighting, nighttime glaring issue should be evaluated for impact to night operations and impact to control tower nighttime visibility. Verify acceptability of design with Airfield Operations as part of 65% submission.
AR-11 | Provide roof top Antenna Platform with antennae anchoring. Provide access preferably from interior space or by exterior ladder.
Legend:
Lessons Learned Item - for designer reference and discussion with users, DPW, etc.
Required COS Compliance item - to be addressed and reviewed at each submission

## Equipment
Equipment
# | Compliance Item | Impacts / Details | 35% | 65% | 100% | COS Notes
EQ-01 | All equipment is to be shown and identified starting at first design submisison (35% +/-). USACE Standard FFE Nomenclature for equipment shown on COS equipment plans are to be used without exception. If additional equipment is required, contact COS for help in generating designation. Refer to: https://www.wbdg.org/ffc/army-coe/policies-and-guidance-army-design-and-construction/usace-furniture-item-descriptions-and-standard-nomenclature All projects are to be submitted to Huntsville Center at 65% and 100% submisisons for coordination and compliance review. | Contact Stephanie Hardin (Stephanie.R.Hardin@usace.army.mil - (256) 895-1512) at Huntsville Center to coordinate submission requirements and budgets.
EQ-02 | Ensure UFGS SECTION 01 78 23 requires Occupant Operations Manual and Video Recordings of all Building System Training for all Hangar Door and Crane Equipment. | Post-occupancy assessments of recent newly constructed hangars reveal that building users often have no idea of the available features for their new buildings such as counduits for antenna cables, environmental controls, etc. and typically "make do" by circumventing safety and energy saving features.
EQ-03 | Some units report they are required to maintain equipment such as Fire Extinguishers that would normally be maintained by DPW. Coordinate with unit at 35% to discover if they have this requirement and if so, what utility requirements are associated with the equipment. | Pre-design activities at installations reveal that units are having to purchase and maintain fire extinguisher filling machines and other such specialty equipment which require dedicated 120/208 3P circuits. This function historically has been provided by base fire stations or DPW.
EQ-04 | All stools and chairs in admin and shop spaces must have casters.
Legend:
Lessons Learned Item - for designer reference and discussion with users, DPW, etc.
Required COS Compliance item - to be addressed and reviewed at each submisison

## Fire Protection
Fire Protection
# | Compliance Item | Impacts / Details | 35% | 65% | 100% | COS Notes
FP-01 | Ensure compliance with UFC 4-211-01 Aircraft Maintenance Hangars
FP-02 | Ensure no unrelated utilities (drains, ducts, conduit, etc.) route over or through elevator shaft or in/through elevator machine room. | This is an Elevator Code Requirement not found in the Building Codes or Fire Codes.
FP-03 | Ensure UFGS section 21 13 25 "HIGH-EXPANSION FOAM SYSTEM, FIRE PROTECTION" includes all required checklist items under paragraph 3.34.1. | Recent hangar projects have not listed required items in section leading to change orders.
FP-04 | Ensure UFGS SECTION 01 78 23 requires Occupant Operations Manual and Video Recordings of all Fire Suppression and Fire Alarm Equipment. | Post-occupancy assessments of recent newly constructed hangars reveal that building users often have no idea of the available features for their new buildings and typically "make do" by circumventing safety and energy saving features.
FP-05 | Verify IR flame detector coverage of the hangar bays meets UFC 4-211-01 requirement when all aircraft modules are occupied: "Provide a sufficient number of optical flame detectors around the perimeter of the hangar bay, such that all portions of the hangar bay are within the range and cone-of-vision of at least three detectors." | Failure to design around an occupied hangar bay may lead to change order for additional flame detectors.
FP-06 | Verify UFC 4-211-01 Army specific requirement for additional manual foam stop stations: "In addition to stations required by 3-6.19.9: Manual Foam Stop Stations, provide a manual foam stop station in the corridor of each required exit from the hangar bay through the support space." | Failure to include may lead to change order for additional stop stations.
FP-07 | Are bridge cranes shown on all plans , sections and coordinated with other disciplines?
Legend:
Lessons Learned Item - for designer reference and discussion with users, DPW, etc.
Required COS Compliance item - to be addressed and reviewed at each submission

## Mechanical
Mechanical
# | Compliance Item | Impacts / Details | 35% | 65% | 100% | COS Notes
ME-01 | Provide floor drains at all eye wash / emergancy shower stations unless restricted by DPW written environmental policy. | UFC 4-211-01 paragraph 3-5.5.1 states that this is a user option. COS Post Occupancy Surveys consistently reveal user desire for drains after occupation as eyewash stations are tested weekly; drains facilitate testing without requiring extensive clean up of water.
ME-02 | Are controls for maintenance bay heating system occupant accessible and occupant controllable from within the hangar? | Some maintenance activities are temperature sensitive and may require the temperature in the maintenance bay to be temporarily elevated. Local control is preferable to eliminate the need for submitting a work order to DPW (often multi-day response)
ME-03 | Provide hose bibbs at all utility stands to allow washing of aircraft in all maintenance modules. | Some Units assign modules by company so all bays need ability to wash aircraft inside during inclement weather.
ME-04 | Provide dedicated exhaust system with filtering for Blade Shop. | Air must not be recirculated due to hexavalent chromium contamination issues.
ME-05 | Ensure no unrelated utilities (drains, ducts, conduit, etc.) route over or through elevator shaft or in/through elevator machine room. | This is an Elevator Code Requirement not found in the Building Codes or Fire Codes.
ME-06 | Ensure UFGS SECTION 01 78 23 requires Occupant Operations Manual and Video Recordings of all Building System Training for all HVAC, Compressed Air, Plumbing controls and Equipment. | Post-occupancy assessments of recent newly constructed hangars reveal that building users often have no idea of the available features for their new buildings such as conduits for antenna cables, environmental controls, etc. and typically "make do" by circumventing safety and energy saving features.
ME-07 | Are bridge cranes shown on all plans , sections and coordinated with other disciplines?
ME-08 | Provide hose bibbs at exterior covered storage areas.
Legend:
Lessons Learned Item - for designer reference and discussion with users, DPW, etc.
Required COS Compliance item - to be addressed and reviewed at each submission

## Electrical
Electrical
# | Compliance Item | Impacts / Details | 35% | 65% | 100% | COS Notes
EL-01 | Ensure no unrelated utilities (drains, ducts, conduit, etc.) route over or through elevator shaft or in/through elevator machine room. | This is an Elevator Code Requirement not found in the Building Codes or Fire Codes.
EL-02 | Include drawings and details for GSE and ASIOE covered storage areas | Provide lighting and power at all exterior covered storage.
EL-03 | Ensure UFGS SECTION 01 78 23 requires Occupant Operations Manual and Video Recordings of all Building System Training for all Lighting Controls, Equipment and infrastructure provisions such as critical pathways. | Post-occupancy assessments of recent newly constructed hangars reveal that building users often have no idea of the available features for their new buildings such as conduits for antenna cables, environmental controls, etc. and typically "make do" by circumventing safety and energy saving features.
EL-04 | Verify fixed 400Hz/28VDC systems are provided; not carts | Use of carts requires a waiver from the COS.
EL-05 | Verify quantity and locations of aircraft utility pedestals; as shown if Standard Design is used or at a minimum one between every two aircraft if no Standard Design is available.
EL-06 | Verify all electrical and comm requirements on the pedestals meet the COS requirements.
EL-07 | Verify separate service entrances are provided for all fire pumps and foam fire pumps.
EL-08 | Verify hangar doors are connected ahead of main disconnect and provided with a manual transfer switch and portable generator connection IAW UFC 4-211-01.
EL-09 | Verify Army specific requirement of UFC 4-211-01 that: "All electrical equipment in the hangar bay is required to be in a NEMA 250 Type 3R or weather proof enclosure."
EL-10 | Verify all shop equipment electrical connections with Unit and Mission-Unique Equipment
EL-11 | Verify Class 1 Division 2 requirement for all spaces directly connected to hangar bay (no intervening airlocks, vestibules).
EL-12 | Verify Exterior connection for mobile shop sets.
EL-13 | All power receptacles on utility stands to be GFI
Legend:
Lessons Learned Item - for designer reference and discussion with users, DPW, etc.
Required COS Compliance item - to be addressed and reviewed at each submission

## Security
Security
# | Compliance Item | Impacts / Details | 35% | 65% | 100% | COS Notes
ES-01 | Verify intrusion detection system (IDS) locations with COS standard design room data sheets.
ES-02 | Verify CCTV coverage with COS standard design requirement.
ES-03 | Discuss and document responsibility for funding of IDS, CCTV with unit personnel at every design submission review
Legend:
Lessons Learned Item - for designer reference and discussion with users, DPW, etc.
Required COS Compliance item - to be addressed and reviewed at each submisison

## Telecomm
Telecommunications
# | Compliance Item | Impacts / Details | 35% | 65% | 100% | COS Notes
TC-01 | Verify SIPR drop quantities and locations with COS standard design room data sheets. Only provide additional drops where required by unit with approval / confirmation of NEC that SIPR system can be installed and operated upon occupation. Provide documentation in Design Analysis of coordination with unit, NEC, DPW. | SIPR drops require rigorous and regular inspection protocols; limiting number of drops eases burden of inspections.
TC-02 | Verify COS requirement for three separate networks; unclassified NIPR network, unclassified Logistics Information System (LIS, formally ACN), and classified SIPR network. All three systems require separate telecommunications rooms, but the unclassified networks may share pathways and outlet plates. The classified SIPR network requires a PDS distribution system. A separate Voice (copper) systems will be required if VOIP is unavailable.
TC-03 | Verify unclassified networks drop requirements with COS standard design room data sheets.
TC-04 | Provide roof top Antenna Platform with antennae anchoring. Provide access preferably from interior space or by exterior ladder.
Legend:
Lessons Learned Item - for designer reference and discussion with users, DPW, etc.
Required COS Compliance item - to be addressed and reviewed at each submission